{"text_format":"2","workbook":"xlsx","n_sheets":5,"sheets":["基本信息格式","总召唤命令","时钟同步读取","101规约解析","104规约解析"],"not_rendered":{"charts":0,"images":0,"macros":0,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"run_cost":"one","rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"基本信息格式","index":0,"n_rows":93,"n_cols":11,"rows_kept":93,"cut":false,"hidden":false,"merged":[[0,0,0,10],[2,3,2,10],[3,1,3,10],[5,7,5,10],[6,7,6,10],[7,7,7,10],[8,7,8,10],[9,7,9,10],[11,2,11,10],[13,2,13,10],[15,3,15,10],[19,0,19,10],[21,3,21,10],[23,3,23,10],[25,3,25,10],[27,3,27,10],[30,7,30,10],[31,7,31,10],[32,7,32,10],[33,7,33,10],[34,7,34,10],[36,2,36,10],[38,0,38,10],[39,5,39,7],[40,5,40,7],[41,5,41,7],[42,5,42,7],[43,5,43,7],[44,5,44,7],[45,5,45,7],[46,5,46,7],[49,4,49,10],[50,4,50,10],[51,4,51,10],[52,4,52,10],[54,5,54,10],[55,5,55,10],[56,5,56,10],[57,5,57,10],[58,5,58,10],[59,5,59,10],[60,5,60,10],[61,5,61,10],[62,5,62,10],[63,5,63,10],[64,5,64,10],[65,5,65,10],[66,5,66,10],[67,5,67,10],[68,5,68,10],[69,5,69,10],[70,5,70,10],[71,5,71,10],[72,5,72,10],[73,5,73,10],[75,2,75,10],[77,2,77,10],[79,2,79,10],[82,3,82,10],[83,3,83,10],[84,5,84,10],[85,6,85,10],[86,3,86,5],[86,6,86,10],[87,7,87,10],[88,4,88,10],[90,2,90,10],[92,3,92,10],[4,0,9,0],[29,0,34,0],[39,0,46,0],[48,0,52,0],[54,0,73,0],[81,0,88,0],[4,1,9,1],[29,1,34,1],[39,1,46,1],[48,1,52,1],[54,1,73,1],[81,1,88,1],[8,2,9,2],[33,2,34,2],[39,2,46,2],[54,2,73,2],[39,8,46,10]]}
["固定帧长格式（6个字节）"]
[]
["启动字符","1字节","取值","10H"]
[null,"平衡链路，上行（客户端到主机）"]
["控制域C","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x40","&0x20","&0x10","&0x0f"]
[null,null,"符号表示","DIR","PRM","RES","DFC","FC"]
[null,null,"意义","传输方向","启动标志","保留位","数据流控制位","平衡链路功能码"]
[null,null,"值及功能","1，上行","1.报文来自启动站","取值0","1.从动站不能接收后续报文","上行，规约中无对应功能码"]
[{"$nulls":4},"0.报文来自从动站",null,"0.从动站可以接收后续报文"]
[]
["地址域A","2字节","选址范围为0001H～FFFFH(65535个)， FFFFH为广播地址，0000H为无效地址"]
[]
["校验和CS","1字节","是控制域C、地址域A的字节的八位位组算术和，不考虑溢出位，即： CS＝（C＋A）MOD 256"]
[]
["结束字符","1字节","取值","16H"]
[]
[]
[]
["可变帧长格式（L+6个字节）"]
[]
["启动字符","1字节","取值","68H"]
[]
["报文长度L","1字节","取值","从控制域到应用服务数据单元结束的字节总长度"]
[]
["报文长度L","1字节","取值","第2个报文长度L与第一个报文长度L相同"]
[]
["启动字符","1字节","取值","68H"]
[]
["控制域C","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x40","&0x20","&0x10","&0x0f"]
[null,null,"符号表示","DIR","PRM","RES","DFC","FC"]
[null,null,"意义","传输方向","启动标志","保留位","数据流控制位","平衡链路功能码"]
[null,null,"值及功能","1，上行","1.报文来自启动站","取值0","1.从动站不能接收后续报文","上行，规约中无对应功能码"]
[{"$nulls":4},"0.报文来自从动站",null,"0.从动站可以接收后续报文"]
[]
["地址域A","2字节","选址范围为0001H～FFFFH(65535个)， FFFFH为广播地址，0000H为无效地址"]
[]
["(以下是应用服务数据单元 ASDU)"]
["类型标识","1字节","取值",1,"0x01","单点信息",null,null,"监视方向的过程信息"]
[null,null,null,3,"0x03","双点信息 "]
[null,null,null,9,"0x09","测量值，归一化值"]
[null,null,null,11,"0x0B","测量值，标度化值"]
[null,null,null,13,"0x0D","测量值，短浮点数"]
[null,null,null,30,"0x1E","带CP56Time2a时标的单点信息"]
[null,null,null,31,"0x1F","带CP56Time2a时标的双点信息"]
[null,null,null,70,"0x46","初始化结束"]
[]
["可变结构限定词","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x7F"]
[null,null,"符号表示","SQ","number"]
[null,null,"意义","地址连续性","应用服务数据单元信息元素(单个信息元素或同类信息元素组合)的数目"]
[null,null,"值及功能","0.地址不连续\n1.地址连续","<0>∶＝应用服务数据单元不含信息对象;<1..127>∶＝应用服务数据单元信息元素的数目"]
[]
["传输原因","1字节","取值",0,"0x00","未用"]
[null,null,null,1,"0x01","周期、循环 "]
[null,null,null,2,"0x02","背景扫描"]
[null,null,null,3,"0x03","突发(自发) "]
[null,null,null,4,"0x04","初始化"]
[null,null,null,5,"0x05","请求或者被请求"]
[null,null,null,6,"0x06","激活"]
[null,null,null,7,"0x07","激活确认"]
[null,null,null,8,"0x08","停止激活 "]
[null,null,null,9,"0x09","停止激活确认"]
[null,null,null,10,"0x0a","激活终止 "]
[null,null,null,13,"0x0d","文件传输"]
[null,null,null,20,"0x14","响应站召唤"]
[null,null,null,44,"0x2c","未知的类型标识"]
[null,null,null,45,"0x2d","未知的传送原因"]
[null,null,null,46,"0x2e","未知的应用服务数据单元公共地址"]
[null,null,null,47,"0x2f","未知的信息对象地址"]
[null,null,null,48,"0x30","遥控执行软压板状态错误"]
[null,null,null,49,"0x31","遥控执行时间戳错误"]
[null,null,null,50,"0x32","遥控执行数字签名认证错误"]
[]
["应用服务数据单元公共地址","2字节","是一个系统参数，每一个配电终端对应唯一的一个值"]
[]
["信息对象地址i","2字节","信息对象地址位二个字节"]
[]
["信息元素i","1字节","根据信息格式要求表示"]
[]
["时标CP56Time2a\ni","7字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"第1字节","毫秒(低8位)"]
[null,null,"第2字节","毫秒(高8位）"]
[null,null,"第3字节",0,0,"分钟(0~59）"]
[null,null,"第4字节",0,0,0,"小时（0~23）"]
[null,null,"第5字节","星期（1~7）",null,null,"日（0~31）"]
[null,null,"第6字节",0,0,0,0,"月（1~12）"]
[null,null,"第7字节",0,"年（0~99）"]
[]
["校验和CS","1字节","是控制域C、地址域A、应用服务数据单元ASDU的字节的八位位组算术和，不考虑溢出位，即：CS＝（C＋A+ ASDU）MOD 256"]
[]
["结束字符","1字节","取值","16H"]

{"sheet":"总召唤命令","index":1,"n_rows":76,"n_cols":11,"rows_kept":76,"cut":false,"hidden":false,"merged":[[1,0,1,10],[3,3,3,10],[5,3,5,10],[7,3,7,10],[9,3,9,10],[12,7,12,10],[13,7,13,10],[14,7,14,10],[15,7,15,10],[16,7,16,10],[18,2,18,10],[20,0,20,10],[21,5,21,7],[22,5,22,7],[23,5,23,7],[24,5,24,7],[25,5,25,7],[26,5,26,7],[27,5,27,7],[28,5,28,7],[29,5,29,7],[29,8,29,10],[32,4,32,10],[33,4,33,10],[34,4,34,10],[35,4,35,10],[37,5,37,10],[38,5,38,10],[39,5,39,10],[40,5,40,10],[41,5,41,10],[42,5,42,10],[43,5,43,10],[44,5,44,10],[45,5,45,10],[46,5,46,10],[47,5,47,10],[48,5,48,10],[49,5,49,10],[50,5,50,10],[51,5,51,10],[52,5,52,10],[53,5,53,10],[54,5,54,10],[55,5,55,10],[56,5,56,10],[58,2,58,10],[60,2,60,10],[62,2,62,10],[65,3,65,10],[66,3,66,10],[67,5,67,10],[68,6,68,10],[69,3,69,5],[69,6,69,10],[70,7,70,10],[71,4,71,10],[73,2,73,10],[75,3,75,10],[11,0,16,0],[21,0,29,0],[31,0,35,0],[37,0,56,0],[64,0,71,0],[11,1,16,1],[21,1,29,1],[31,1,35,1],[37,1,56,1],[64,1,71,1],[15,2,16,2],[21,2,29,2],[37,2,56,2],[21,8,28,10]]}
[]
["总召唤应用报文结构"]
[]
["启动字符","1字节","取值","68H"]
[]
["报文长度L","1字节","取值","从控制域到应用服务数据单元结束的字节总长度"]
[]
["报文长度L","1字节","取值","第2个报文长度L与第一个报文长度L相同"]
[]
["启动字符","1字节","取值","68H"]
[]
["控制域C","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x40","&0x20","&0x10","&0x0f"]
[null,null,"符号表示","DIR","PRM","RES","DFC","FC"]
[null,null,"意义","传输方向","启动标志","保留位","数据流控制位","平衡链路功能码"]
[null,null,"值及功能","1，上行","1.报文来自启动站","取值0","1.从动站不能接收后续报文","上行，规约中无对应功能码"]
[{"$nulls":4},"0.报文来自从动站",null,"0.从动站可以接收后续报文"]
[]
["地址域A","2字节","选址范围为0001H～FFFFH(65535个)， FFFFH为广播地址，0000H为无效地址"]
[]
["(以下是应用服务数据单元 ASDU)"]
["类型标识TI","1字节","取值",1,"0x01","单点信息",null,null,"监视方向的过程信息"]
[null,null,null,3,"0x03","双点信息 "]
[null,null,null,9,"0x09","测量值，归一化值"]
[null,null,null,11,"0x0B","测量值，标度化值"]
[null,null,null,13,"0x0D","测量值，短浮点数"]
[null,null,null,30,"0x1E","带CP56Time2a时标的单点信息"]
[null,null,null,31,"0x1F","带CP56Time2a时标的双点信息"]
[null,null,null,70,"0x46","初始化结束"]
[null,null,null,100,"0x64","召唤命令",null,null,"系统命令 总召唤"]
[]
["可变结构限定词","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x7F"]
[null,null,"符号表示","SQ","number"]
[null,null,"意义","地址连续性","应用服务数据单元信息元素(单个信息元素或同类信息元素组合)的数目"]
[null,null,"值及功能","0.地址不连续\n1.地址连续","<0>∶＝应用服务数据单元不含信息对象;<1..127>∶＝应用服务数据单元信息元素的数目"]
[]
["传输原因","1字节","取值",0,"0x00","未用"]
[null,null,null,1,"0x01","周期、循环 "]
[null,null,null,2,"0x02","背景扫描"]
[null,null,null,3,"0x03","突发(自发) "]
[null,null,null,4,"0x04","初始化"]
[null,null,null,5,"0x05","请求或者被请求"]
[null,null,null,6,"0x06","激活"]
[null,null,null,7,"0x07","激活确认"]
[null,null,null,8,"0x08","停止激活 "]
[null,null,null,9,"0x09","停止激活确认"]
[null,null,null,10,"0x0a","激活终止 "]
[null,null,null,13,"0x0d","文件传输"]
[null,null,null,20,"0x14","响应站召唤（总召唤）"]
[null,null,null,44,"0x2c","未知的类型标识"]
[null,null,null,45,"0x2d","未知的传送原因"]
[null,null,null,46,"0x2e","未知的应用服务数据单元公共地址"]
[null,null,null,47,"0x2f","未知的信息对象地址"]
[null,null,null,48,"0x30","遥控执行软压板状态错误"]
[null,null,null,49,"0x31","遥控执行时间戳错误"]
[null,null,null,50,"0x32","遥控执行数字签名认证错误"]
[]
["应用服务数据单元公共地址","2字节","是一个系统参数，每一个配电终端对应唯一的一个值"]
[]
["信息对象地址","2字节","信息对象地址位二个字节（总召唤，信息地址为0）"]
[]
["信息元素i","1字节","召唤限定词（总召唤取值20）"]
[]
["时标CP56Time2a\nI\n（总召唤无时标）","7字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"第1字节","毫秒(低8位)"]
[null,null,"第2字节","毫秒(高8位）"]
[null,null,"第3字节",0,0,"分钟(0~59）"]
[null,null,"第4字节",0,0,0,"小时（0~23）"]
[null,null,"第5字节","星期（1~7）",null,null,"日（0~31）"]
[null,null,"第6字节",0,0,0,0,"月（1~12）"]
[null,null,"第7字节",0,"年（0~99）"]
[]
["校验和CS","1字节","是控制域C、地址域A、应用服务数据单元ASDU的字节的八位位组算术和，不考虑溢出位，即：CS＝（C＋A+ ASDU）MOD 256"]
[]
["结束字符","1字节","取值","16H"]

{"sheet":"时钟同步读取","index":2,"n_rows":77,"n_cols":11,"rows_kept":77,"cut":false,"hidden":false,"merged":[[1,0,1,10],[3,3,3,10],[5,3,5,10],[7,3,7,10],[9,3,9,10],[12,7,12,10],[13,7,13,10],[14,7,14,10],[15,7,15,10],[16,7,16,10],[18,2,18,10],[20,0,20,10],[21,5,21,7],[22,5,22,7],[23,5,23,7],[24,5,24,7],[25,5,25,7],[26,5,26,7],[27,5,27,7],[28,5,28,7],[29,5,29,7],[29,8,29,10],[30,5,30,7],[30,8,30,10],[33,4,33,10],[34,4,34,10],[35,4,35,10],[36,4,36,10],[38,5,38,10],[39,5,39,10],[40,5,40,10],[41,5,41,10],[42,5,42,10],[43,5,43,10],[44,5,44,10],[45,5,45,10],[46,5,46,10],[47,5,47,10],[48,5,48,10],[49,5,49,10],[50,5,50,10],[51,5,51,10],[52,5,52,10],[53,5,53,10],[54,5,54,10],[55,5,55,10],[56,5,56,10],[57,5,57,10],[59,2,59,10],[61,2,61,10],[63,2,63,10],[66,3,66,10],[67,3,67,10],[68,5,68,10],[69,6,69,10],[70,3,70,5],[70,6,70,10],[71,7,71,10],[72,4,72,10],[74,2,74,10],[76,3,76,10],[11,0,16,0],[21,0,30,0],[32,0,36,0],[38,0,57,0],[65,0,72,0],[11,1,16,1],[21,1,30,1],[32,1,36,1],[38,1,57,1],[65,1,72,1],[15,2,16,2],[21,2,30,2],[38,2,57,2],[21,8,28,10]]}
[]
["时钟同步应用报文结构"]
[]
["启动字符","1字节","取值","68H"]
[]
["报文长度L","1字节","取值","从控制域到应用服务数据单元结束的字节总长度"]
[]
["报文长度L","1字节","取值","第2个报文长度L与第一个报文长度L相同"]
[]
["启动字符","1字节","取值","68H"]
[]
["控制域C","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x40","&0x20","&0x10","&0x0f"]
[null,null,"符号表示","DIR","PRM","RES","DFC","FC"]
[null,null,"意义","传输方向","启动标志","保留位","数据流控制位","平衡链路功能码"]
[null,null,"值及功能","1，上行","1.报文来自启动站","取值0","1.从动站不能接收后续报文","上行，规约中无对应功能码"]
[{"$nulls":4},"0.报文来自从动站",null,"0.从动站可以接收后续报文"]
[]
["地址域A","2字节","选址范围为0001H～FFFFH(65535个)， FFFFH为广播地址，0000H为无效地址"]
[]
["(以下是应用服务数据单元 ASDU)"]
["类型标识TI","1字节","取值",1,"0x01","单点信息",null,null,"监视方向的过程信息"]
[null,null,null,3,"0x03","双点信息 "]
[null,null,null,9,"0x09","测量值，归一化值"]
[null,null,null,11,"0x0B","测量值，标度化值"]
[null,null,null,13,"0x0D","测量值，短浮点数"]
[null,null,null,30,"0x1E","带CP56Time2a时标的单点信息"]
[null,null,null,31,"0x1F","带CP56Time2a时标的双点信息"]
[null,null,null,70,"0x46","初始化结束"]
[null,null,null,100,"0x64","召唤命令",null,null,"系统命令 总召唤"]
[null,null,null,103,"0x64","时钟同步/读取命令",null,null,"系统命令 时钟同步"]
[]
["可变结构限定词","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x7F"]
[null,null,"符号表示","SQ","number"]
[null,null,"意义","地址连续性","应用服务数据单元信息元素(单个信息元素或同类信息元素组合)的数目"]
[null,null,"值及功能","0.地址不连续\n1.地址连续","<0>∶＝应用服务数据单元不含信息对象;<1..127>∶＝应用服务数据单元信息元素的数目"]
[]
["传输原因","1字节","取值",0,"0x00","未用"]
[null,null,null,1,"0x01","周期、循环 "]
[null,null,null,2,"0x02","背景扫描"]
[null,null,null,3,"0x03","突发(自发) "]
[null,null,null,4,"0x04","初始化"]
[null,null,null,5,"0x05","请求或者被请求"]
[null,null,null,6,"0x06","激活"]
[null,null,null,7,"0x07","激活确认"]
[null,null,null,8,"0x08","停止激活 "]
[null,null,null,9,"0x09","停止激活确认"]
[null,null,null,10,"0x0a","激活终止 "]
[null,null,null,13,"0x0d","文件传输"]
[null,null,null,20,"0x14","响应站召唤（总召唤）"]
[null,null,null,44,"0x2c","未知的类型标识"]
[null,null,null,45,"0x2d","未知的传送原因"]
[null,null,null,46,"0x2e","未知的应用服务数据单元公共地址"]
[null,null,null,47,"0x2f","未知的信息对象地址"]
[null,null,null,48,"0x30","遥控执行软压板状态错误"]
[null,null,null,49,"0x31","遥控执行时间戳错误"]
[null,null,null,50,"0x32","遥控执行数字签名认证错误"]
[]
["应用服务数据单元公共地址","2字节","是一个系统参数，每一个配电终端对应唯一的一个值"]
[]
["信息对象地址","2字节","信息对象地址位二个字节（总召唤，信息地址为0）（时钟同步，信息地址为0）"]
[]
["信息元素i","1字节","召唤限定词（总召唤取值20）（时钟同步，信息元素无）"]
[]
["时标CP56Time2a\nI\n（总召唤无时标）\n（时钟同步带时标）","7字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"第1字节","毫秒(低8位)"]
[null,null,"第2字节","毫秒(高8位）"]
[null,null,"第3字节",0,0,"分钟(0~59）"]
[null,null,"第4字节",0,0,0,"小时（0~23）"]
[null,null,"第5字节","星期（1~7）",null,null,"日（0~31）"]
[null,null,"第6字节",0,0,0,0,"月（1~12）"]
[null,null,"第7字节",0,"年（0~99）"]
[]
["校验和CS","1字节","是控制域C、地址域A、应用服务数据单元ASDU的字节的八位位组算术和，不考虑溢出位，即：CS＝（C＋A+ ASDU）MOD 256"]
[]
["结束字符","1字节","取值","16H"]

{"sheet":"101规约解析","index":3,"n_rows":155,"n_cols":11,"rows_kept":155,"cut":false,"hidden":false,"merged":[[2,0,2,10],[4,3,4,10],[7,7,7,10],[8,7,8,10],[9,7,9,10],[13,7,13,10],[14,7,14,10],[15,7,15,10],[19,3,19,10],[20,3,20,5],[20,7,20,10],[21,3,21,5],[21,7,21,10],[22,3,22,5],[22,7,22,10],[23,3,23,5],[23,7,23,10],[24,3,24,5],[24,7,24,10],[25,3,25,5],[25,7,25,10],[26,3,26,5],[26,7,26,10],[28,2,28,10],[30,2,30,10],[32,3,32,10],[36,0,36,10],[38,3,38,10],[40,3,40,10],[42,3,42,10],[44,3,44,10],[47,7,47,10],[48,7,48,10],[49,7,49,10],[53,7,53,10],[54,7,54,10],[55,7,55,10],[59,3,59,10],[60,3,60,5],[60,7,60,10],[61,3,61,5],[61,7,61,10],[62,3,62,5],[62,7,62,10],[63,3,63,5],[63,7,63,10],[64,3,64,5],[64,7,64,10],[65,3,65,5],[65,7,65,10],[66,3,66,5],[66,7,66,10],[68,2,68,10],[70,0,70,10],[71,5,71,7],[72,5,72,7],[73,5,73,7],[74,5,74,7],[75,5,75,7],[76,5,76,7],[77,5,77,7],[78,5,78,7],[79,5,79,7],[80,5,80,7],[81,5,81,7],[82,5,82,7],[83,5,83,7],[84,5,84,7],[84,8,84,10],[85,5,85,7],[85,8,85,10],[86,5,86,7],[86,8,86,10],[87,5,87,7],[87,8,87,10],[90,4,90,10],[91,4,91,10],[92,4,92,10],[93,4,93,10],[95,5,95,10],[96,5,96,10],[97,5,97,10],[98,5,98,10],[99,5,99,10],[100,5,100,10],[101,5,101,10],[102,5,102,10],[103,5,103,10],[104,5,104,10],[105,5,105,10],[106,5,106,10],[107,5,107,10],[108,5,108,10],[109,5,109,10],[110,5,110,10],[111,5,111,10],[112,5,112,10],[113,5,113,10],[114,5,114,10],[116,2,116,10],[118,2,118,10],[122,9,122,10],[124,9,124,10],[125,3,125,10],[126,3,126,10],[127,3,127,10],[128,3,128,10],[129,3,129,10],[130,2,130,10],[131,2,131,10],[132,3,132,10],[133,3,133,10],[134,3,134,10],[135,3,135,10],[137,4,137,10],[138,4,138,10],[139,2,139,10],[143,3,143,10],[144,3,144,10],[145,5,145,10],[146,6,146,10],[147,3,147,5],[147,6,147,10],[148,7,148,10],[149,4,149,10],[150,0,150,10],[152,2,152,10],[154,3,154,10],[6,0,17,0],[46,0,57,0],[71,0,87,0],[89,0,93,0],[95,0,114,0],[120,0,130,0],[132,0,139,0],[142,0,149,0],[6,1,11,1],[12,1,17,1],[46,1,51,1],[52,1,57,1],[71,1,87,1],[89,1,93,1],[95,1,114,1],[120,1,124,1],[126,1,129,1],[132,1,138,1],[142,1,149,1],[10,2,11,2],[16,2,17,2],[50,2,51,2],[56,2,57,2],[71,2,87,2],[95,2,114,2],[136,2,138,2],[10,3,11,3],[16,3,17,3],[50,3,51,3],[56,3,57,3],[10,5,11,5],[16,5,17,5],[50,5,51,5],[56,5,57,5],[78,8,79,10],[80,8,83,10],[71,8,77,10],[56,7,57,10],[50,7,51,10],[10,7,11,10],[16,7,17,10]]}
[]
[]
["固定帧长格式（6个字节）"]
[]
["启动字符","1字节","取值","10H"]
[]
["控制域C\n（1字节）","（上行）","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x40","&0x20","&0x10","&0x0f"]
[null,null,"符号表示","DIR","PRM","RES","DFC","FC"]
[null,null,"意义","传输方向","启动标志","保留位","数据流控制位","平衡链路功能码"]
[null,null,"值及功能","1，上行","1.报文来自启动站","取值0","1.从动站不能接收后续报文","见附表"]
[{"$nulls":4},"0.报文来自从动站",null,"0.从动站可以接收后续报文"]
[null,"（下行）","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x40","&0x20","&0x10","&0x0f"]
[null,null,"符号表示","DIR","PRM","FCB","FCV","FC"]
[null,null,"意义","传输方向","启动标志","帧计数位","帧计数有效位","平衡链路功能码"]
[null,null,"值及功能","0，下行","1.报文来自启动站","每次传输数据有效该位取反","1.表示FCB有效","见附表"]
[{"$nulls":4},"0.报文来自从动站",null,"0.表示FCB无效"]
[]
[null,null,null,"附表：平衡链路功能码（启动方FC——从动方FC）"]
[null,null,null,"启动方向的功能码和服务FC",null,null,"启动方向的FCV位状态","从动方向所允许的功能码和服务FC"]
[null,null,null,"<0>复位远方链路",null,null,0,"<0>确认：认可     <1>确认：否定认可"]
[null,null,null,"<1>复位用户进程",null,null,0,"<0>确认：认可     <1>确认：否定认可"]
[null,null,null,"<2>发送/确认链路测试功能 ",null,null,0,"<0>确认：认可     <1>确认：否定认可"]
[null,null,null,"<3>发送/确认用户数据",null,null,1,"<0>确认：认可     <1>确认：否定认可"]
[null,null,null,"<4>发送/无回答用户数据",null,null,0,"无回答"]
[null,null,null,"<9>请求/响应请求链路状态",null,null,0,"<11>响应：链路状态"]
[]
["地址域A","2字节","选址范围为0001H～FFFFH(65535个)， FFFFH为广播地址，0000H为无效地址"]
[]
["校验和CS","1字节","是控制域C、地址域A的字节的八位位组算术和，不考虑溢出位，即： CS＝（C＋A）MOD 256"]
[]
["结束字符","1字节","取值","16H"]
[]
[]
[]
["可变帧长格式（L+6个字节）"]
[]
["启动字符","1字节","取值","68H"]
[]
["报文长度L","1字节","取值","从控制域到应用服务数据单元结束的字节总长度"]
[]
["报文长度L","1字节","取值","第2个报文长度L与第一个报文长度L相同"]
[]
["启动字符","1字节","取值","68H"]
[]
["控制域C","1字节\n（上行）","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x40","&0x20","&0x10","&0x0f"]
[null,null,"符号表示","DIR","PRM","RES","DFC","FC"]
[null,null,"意义","传输方向","启动标志","保留位","数据流控制位","平衡链路功能码"]
[null,null,"值及功能","1，上行","1.报文来自启动站","取值0","1.从动站不能接收后续报文","见附表"]
[{"$nulls":4},"0.报文来自从动站",null,"0.从动站可以接收后续报文"]
[null,"1字节\n（下行）","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x40","&0x20","&0x10","&0x0f"]
[null,null,"符号表示","DIR","PRM","FCB","FCV","FC"]
[null,null,"意义","传输方向","启动标志","帧计数位","帧计数有效位","平衡链路功能码"]
[null,null,"值及功能","0，下行","1.报文来自启动站","每次传输数据有效该位取反","1.表示FCB有效","见附表"]
[{"$nulls":4},"0.报文来自从动站",null,"0.表示FCB无效"]
[]
[null,null,null,"附表：平衡链路功能码（启动方FC——从动方FC）"]
[null,null,null,"启动方向的功能码和服务FC",null,null,"启动方向的FCV位状态","从动方向所允许的功能码和服务FC"]
[null,null,null,"<0>复位远方链路",null,null,0,"<0>确认：认可     <1>确认：否定认可"]
[null,null,null,"<1>复位用户进程",null,null,0,"<0>确认：认可     <1>确认：否定认可"]
[null,null,null,"<2>发送/确认链路测试功能 ",null,null,0,"<0>确认：认可     <1>确认：否定认可"]
[null,null,null,"<3>发送/确认用户数据",null,null,1,"<0>确认：认可     <1>确认：否定认可"]
[null,null,null,"<4>发送/无回答用户数据",null,null,0,"无回答"]
[null,null,null,"<9>请求/响应请求链路状态",null,null,0,"<11>响应：链路状态"]
[]
["地址域A","2字节","选址范围为0001H～FFFFH(65535个)， FFFFH为广播地址，0000H为无效地址"]
[]
["(以下是应用服务数据单元 ASDU)"]
["类型标识TI","1字节","取值",1,"0x01","单点信息（遥信）",null,null,"监视方向的过程信息"]
[null,null,null,3,"0x03","双点信息 （遥信）"]
[null,null,null,9,"0x09","测量值，归一化值（遥测）*"]
[null,null,null,11,"0x0B","测量值，标度化值（遥测）"]
[null,null,null,13,"0x0D","测量值，短浮点数（遥测）"]
[null,null,null,30,"0x1E","带CP56Time2a时标的单点信息（遥信带时标）"]
[null,null,null,31,"0x1F","带CP56Time2a时标的双点信息（遥信带时标）"]
[null,null,null,45,"0x2D","单命令（遥控）",null,null,"遥控"]
[null,null,null,46,"0x2E","双命令（遥控）"]
[null,null,null,102,"0x66","读单个参数命令(参数设置)",null,null,"参数设置"]
[null,null,null,132,"0x84","读多个参数命令(参数设置)"]
[null,null,null,48,"0x30","预置/激活单个参数命令(参数设置)"]
[null,null,null,136,"0x88","预置/激活多个参数命令(参数设置)"]
[null,null,null,70,"0x46","初始化结束",null,null,"系统命令 初始化结束"]
[null,null,null,100,"0x64","召唤命令",null,null,"系统命令 总召唤"]
[null,null,null,103,"0x67","时钟同步/读取命令",null,null,"系统命令 时钟同步"]
[null,null,null,105,"0x69","复位进程命令",null,null,"系统命令 复位进程"]
[]
["可变结构限定词","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x7F"]
[null,null,"符号表示","SQ","number"]
[null,null,"意义","地址连续性","应用服务数据单元信息元素(单个信息元素或同类信息元素组合)的数目"]
[null,null,"值及功能","0.地址不连续\n1.地址连续","<0>∶＝应用服务数据单元不含信息对象;<1..127>∶＝应用服务数据单元信息元素的数目"]
[]
["传输原因","1字节","取值",0,"0x00","未用"]
[null,null,null,1,"0x01","周期、循环 （遥测）"]
[null,null,null,2,"0x02","背景扫描（遥信）（遥测）"]
[null,null,null,3,"0x03","突发(自发) （遥信）（遥测）"]
[null,null,null,4,"0x04","初始化完成"]
[null,null,null,5,"0x05","请求或者被请求（遥信被请求）（遥测被请求）"]
[null,null,null,6,"0x06","激活（激活）（遥控、参数设置 控制方向）"]
[null,null,null,7,"0x07","激活确认（激活确认）（遥控、参数设置 监视方向）"]
[null,null,null,8,"0x08","停止激活 （遥控、参数设置 控制方向）"]
[null,null,null,9,"0x09","停止激活确认（遥控、参数设置 监视方向）"]
[null,null,null,10,"0x0a","激活终止 （遥控 监视方向）"]
[null,null,null,13,"0x0d","文件传输"]
[null,null,null,20,"0x14","响应站召唤（总召唤）（遥信响应总召唤）（遥测响应总召唤）"]
[null,null,null,44,"0x2c","未知的类型标识（遥控、参数设置 监视方向）"]
[null,null,null,45,"0x2d","未知的传送原因（遥控、参数设置 监视方向）"]
[null,null,null,46,"0x2e","未知的应用服务数据单元公共地址（遥控、参数设置 监视方向）"]
[null,null,null,47,"0x2f","未知的信息对象地址（遥控、参数设置 监视方向）"]
[null,null,null,48,"0x30","遥控执行软压板状态错误"]
[null,null,null,49,"0x31","遥控执行时间戳错误"]
[null,null,null,50,"0x32","遥控执行数字签名认证错误"]
[]
["应用服务数据单元公共地址","2字节","是一个系统参数，每一个配电终端对应唯一的一个值"]
[]
["信息对象地址\n（单个或多个）","2字节","信息对象地址位二个字节（总召唤，信息地址为0）（时钟同步，信息地址为0）（复位进程地址为0）（初始化地址为0）"]
[]
["信息元素\n（可能是单个\n或多个\n信息元素）","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"单点遥信","0.有效\n1.无效","0.当前值\n1.非当前值","0.未被取代\n1.被取代","0.未被闭锁\n1.被闭锁","备用","备用","备用","0.开关分\n1.开关合"]
[null,null,"双点遥信","0.有效\n1.无效","0.当前值\n1.非当前值","0.未被取代\n1.被取代","0.未被闭锁\n1.被闭锁","备用","备用","0.不确定或中间状态\n1.确定开关分\n2.确定开关合\n3.不确定"]
[null,null,"遥控\n单命令","0.遥控执行命令\n1.遥控选择命令","备用","备用","备用","备用","备用","备用","0.开关分\n1.开关合"]
[null,null,"遥控\n双命令","0.遥控执行命令\n1.遥控选择命令","备用","备用","备用","备用","备用","0.不允许，有错误\n1.开关分\n2.开关合\n3.不允许，有错误"]
[null,"2字节","遥测","链路层传输顺序为低位在前，高位在后；低字节在前，高字节在后。如：69 01应该是01 69，即二进制0000 0001 0110 1001，转换成10进制是361"]
[null,"参数设置\n4字节","读取单个参数","在控制方向：空，在监视方向：返回参数（信息值为4个字节）"]
[null,null,"读取多个参数","在控制方向：空，在监视方向：返回参数（信息值1为4个字节，信息值n为4个字节）"]
[null,null,"预置/激活单个参数","在控制方向：参数值,在监视方向：返回参数镜像（信息值为4个字节）,后缀设定命令限定词1字节"]
[null,null,"预置/激活多个参数","在控制方向：参数值,在监视方向：返回参数镜像（信息值1为4个字节,信息值n为4个字节）,后缀设定命令限定词1字节"]
[null,"描述","总召唤无此项，时钟同步无此项，复位进程无此项，初始化结束无此项，"]
[]
["限定词","1字节","总召唤限定词",20]
[null,null,"复位进程限定词",1]
[null,null,"初始化原因","0.当地电源合上，1.当地手动复位，2.远方复位"]
[null,null,"品质描述词（遥测）","0（每个信息元素后缀1个字节）"]
[null,null,"设置命令限定词\n（参数预置）","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,null,"S/E","QL"]
[null,null,null,"1：选择预置参数\n0：执行激活参数","0:缺省值"]
[null,"描述","时钟同步无此项，遥信无此项，遥控无此项，"]
[]
[]
["时标CP56Time2a\n（总召唤无时标）\n（时钟同步带时标）\n（进程复位无时标）(初始化结束无时标)\n（参数设置无时标）","7字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"第1字节","毫秒(低8位)"]
[null,null,"第2字节","毫秒(高8位）"]
[null,null,"第3字节",0,0,"分钟(0~59）"]
[null,null,"第4字节",0,0,0,"小时（0~23）"]
[null,null,"第5字节","星期（1~7）",null,null,"日（0~31）"]
[null,null,"第6字节",0,0,0,0,"月（1~12）"]
[null,null,"第7字节",0,"年（0~99）"]
["(应用服务数据单元 ASDU结束)"]
[]
["校验和CS","1字节","是控制域C、地址域A、应用服务数据单元ASDU的字节的八位位组算术和，不考虑溢出位，即：CS＝（C＋A+ ASDU）MOD 256"]
[]
["结束字符","1字节","取值","16H"]

{"sheet":"104规约解析","index":4,"n_rows":109,"n_cols":16,"rows_kept":109,"cut":false,"hidden":false,"merged":[[1,0,1,11],[3,3,3,11],[5,3,5,11],[8,4,8,10],[9,4,9,11],[10,4,10,10],[11,4,11,11],[13,4,13,10],[14,4,14,11],[15,4,15,10],[16,4,16,11],[18,4,18,5],[18,6,18,7],[18,8,18,9],[20,4,20,11],[21,4,21,11],[22,4,22,11],[24,5,24,8],[24,9,24,11],[25,5,25,8],[26,5,26,8],[27,5,27,8],[28,5,28,8],[29,5,29,8],[30,5,30,8],[31,5,31,8],[32,5,32,8],[33,5,33,8],[34,5,34,8],[35,5,35,8],[36,5,36,8],[37,5,37,8],[38,5,38,8],[38,9,38,11],[39,5,39,8],[39,9,39,11],[40,5,40,8],[40,9,40,11],[41,5,41,8],[41,9,41,11],[43,10,43,11],[44,4,44,11],[45,4,45,11],[46,4,46,11],[47,4,47,11],[49,10,49,11],[50,7,50,11],[51,7,51,11],[52,7,52,11],[53,7,53,11],[54,7,54,11],[55,7,55,11],[56,7,56,11],[57,7,57,11],[58,7,58,11],[59,7,59,11],[60,7,60,11],[61,7,61,11],[62,7,62,11],[63,7,63,11],[64,7,64,11],[65,7,65,11],[66,7,66,11],[67,7,67,11],[68,7,68,11],[69,7,69,11],[71,2,71,11],[73,10,73,11],[77,3,77,11],[79,10,79,11],[80,10,80,11],[81,9,81,11],[82,10,82,11],[83,9,83,11],[84,3,84,11],[85,3,85,11],[86,3,86,11],[87,3,87,11],[88,3,88,11],[89,2,89,11],[90,2,90,11],[91,3,91,11],[92,3,92,11],[93,3,93,11],[94,3,94,11],[95,10,95,11],[96,4,96,11],[97,4,97,11],[98,2,98,11],[100,10,100,11],[101,3,101,11],[102,3,102,11],[103,5,103,11],[104,6,104,11],[105,3,105,5],[105,6,105,11],[106,7,106,11],[107,4,107,11],[108,2,108,11],[7,0,22,0],[24,0,41,0],[43,0,47,0],[49,0,69,0],[73,0,77,0],[79,0,89,0],[91,0,98,0],[100,0,108,0],[7,1,22,1],[24,1,41,1],[43,1,47,1],[49,1,69,1],[73,1,77,1],[79,1,83,1],[85,1,88,1],[91,1,97,1],[100,1,107,1],[7,2,11,2],[12,2,16,2],[17,2,22,2],[24,2,41,2],[50,2,69,2],[74,2,76,2],[95,2,97,2],[18,3,19,3],[50,3,69,3],[50,4,69,4],[18,10,19,10],[18,11,19,11],[3,13,22,13],[24,13,108,13],[3,15,108,15],[25,9,31,11],[32,9,33,11],[34,9,37,11]]}
[]
["104规约解析"]
[]
["启动字符","1字节","取值","68H",{"$nulls":9},"APCI应用规约控制信息",null,"APDU应用规约数据单元"]
[]
["APDU长度","1字节","取值","最大，253"]
[]
["控制域","4字节","I格式控制域标志\n(编号的信息传输格式)\n(包含ASDU)","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,null,"控制域八位位组1","发送序列号N(S)",{"$nulls":6},0]
[null,null,null,"控制域八位位组2","发送序列号N(S)"]
[null,null,null,"控制域八位位组3","接收序列号N(R)",{"$nulls":6},0]
[null,null,null,"控制域八位位组4","接收序列号N(R)"]
[null,null,"S格式控制域标志\n(编号的监视功能格式)\n（不包含ASDU）","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,null,"控制域八位位组1",0,{"$nulls":6},1]
[null,null,null,"控制域八位位组2",0]
[null,null,null,"控制域八位位组3","接收序列号N(R)",{"$nulls":6},0]
[null,null,null,"控制域八位位组4","接收序列号N®"]
[null,null,"U格式控制域标志\n(不编号的控制功能格式)\n（不包含ASDU）\n（同一时刻TESTFR、STOPDT、STARTDT中只能有一个功能可以被激活）","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,null,"控制域八位位组1","TESTFR",null,"STOPDT",null,"STARTDT",null,1,1]
[{"$nulls":4},"确认","命令","确认","命令","确认","命令"]
[null,null,null,"控制域八位位组2",0]
[null,null,null,"控制域八位位组3",0]
[null,null,null,"控制域八位位组4",0]
[]
["类型标识TI","1字节","取值","10进制","16进制","意义",null,null,null,"类别",null,null,null,"ASDU应用服务数据单元"]
[null,null,null,1,"0x01","单点信息（遥信）",null,null,null,"监视方向的过程信息"]
[null,null,null,3,"0x03","双点信息 （遥信）"]
[null,null,null,9,"0x09","测量值，归一化值（遥测）*"]
[null,null,null,11,"0x0B","测量值，标度化值（遥测）"]
[null,null,null,13,"0x0D","测量值，短浮点数（遥测）"]
[null,null,null,30,"0x1E","带CP56Time2a时标的单点信息（遥信带时标）"]
[null,null,null,31,"0x1F","带CP56Time2a时标的双点信息（遥信带时标）"]
[null,null,null,45,"0x2D","单命令（遥控）",null,null,null,"遥控"]
[null,null,null,46,"0x2E","双命令（遥控）"]
[null,null,null,102,"0x66","读单个参数命令(参数设置)",null,null,null,"参数设置"]
[null,null,null,132,"0x84","读多个参数命令(参数设置)"]
[null,null,null,48,"0x30","预置/激活单个参数命令(参数设置)"]
[null,null,null,136,"0x88","预置/激活多个参数命令(参数设置)"]
[null,null,null,70,"0x46","初始化结束",null,null,null,"系统命令 初始化结束"]
[null,null,null,100,"0x64","召唤命令",null,null,null,"系统命令 总召唤"]
[null,null,null,103,"0x67","时钟同步/读取命令",null,null,null,"系统命令 时钟同步"]
[null,null,null,105,"0x69","复位进程命令",null,null,null,"系统命令 复位进程"]
[]
["可变结构限定词","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值方法","&0x80","&0x7F"]
[null,null,"符号表示","SQ","number"]
[null,null,"意义","地址连续性","应用服务数据单元信息元素(单个信息元素或同类信息元素组合)的数目"]
[null,null,"值及功能","0.地址不连续\n1.地址连续","<0>∶＝应用服务数据单元不含信息对象;<1..127>∶＝应用服务数据单元信息元素的数目"]
[]
["传输原因","2字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"取值及含义","T(test)\n\n0.未试验\n\n1.试验","P/N\n\n0.肯定确认\n\n1.否定确认",0,"0x00","未用"]
[{"$nulls":5},1,"0x01","周期、循环 （遥测）"]
[{"$nulls":5},2,"0x02","背景扫描（遥信）（遥测）"]
[{"$nulls":5},3,"0x03","突发(自发) （遥信）（遥测）"]
[{"$nulls":5},4,"0x04","初始化完成"]
[{"$nulls":5},5,"0x05","请求或者被请求（遥信被请求）（遥测被请求）"]
[{"$nulls":5},6,"0x06","激活（激活）（遥控、参数设置 控制方向）"]
[{"$nulls":5},7,"0x07","激活确认（激活确认）（遥控、参数设置 监视方向）"]
[{"$nulls":5},8,"0x08","停止激活 （遥控、参数设置 控制方向）"]
[{"$nulls":5},9,"0x09","停止激活确认（遥控、参数设置 监视方向）"]
[{"$nulls":5},10,"0x0a","激活终止 （遥控 监视方向）"]
[{"$nulls":5},13,"0x0d","文件传输"]
[{"$nulls":5},20,"0x14","响应站召唤（总召唤）（遥信响应总召唤）（遥测响应总召唤）"]
[{"$nulls":5},44,"0x2c","未知的类型标识（遥控、参数设置 监视方向）"]
[{"$nulls":5},45,"0x2d","未知的传送原因（遥控、参数设置 监视方向）"]
[{"$nulls":5},46,"0x2e","未知的应用服务数据单元公共地址（遥控、参数设置 监视方向）"]
[{"$nulls":5},47,"0x2f","未知的信息对象地址（遥控、参数设置 监视方向）"]
[{"$nulls":5},48,"0x30","遥控执行软压板状态错误"]
[{"$nulls":5},49,"0x31","遥控执行时间戳错误"]
[{"$nulls":5},50,"0x32","遥控执行数字签名认证错误"]
[]
["应用服务数据单元公共地址","2字节","是一个系统参数，每一个配电终端对应唯一的一个值"]
[]
["信息对象地址\n（单个或多个）","3字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"地址表示","7位",{"$nulls":7},"0位"]
[null,null,null,"15位",{"$nulls":7},"8位"]
[null,null,null,"23位",{"$nulls":7},"16位"]
[null,null,"描述","信息对象地址位三个字节（总召唤，信息地址为0）（时钟同步，信息地址为0）（复位进程地址为0）（初始化地址为0）"]
[]
["信息元素\n（可能是单个\n或多个\n信息元素）","1字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"单点遥信","0.有效\n1.无效","0.当前值\n1.非当前值","0.未被取代\n1.被取代","0.未被闭锁\n1.被闭锁","备用","备用","备用","0.开关分\n1.开关合"]
[null,null,"双点遥信","0.有效\n1.无效","0.当前值\n1.非当前值","0.未被取代\n1.被取代","0.未被闭锁\n1.被闭锁","备用","备用","0.不确定或中间状态\n1.确定开关分\n2.确定开关合\n3.不确定"]
[null,null,"遥控\n单命令","0.遥控执行命令\n1.遥控选择命令","备用","备用","备用","备用","备用","备用","0.开关分\n1.开关合"]
[null,null,"遥控\n双命令","0.遥控执行命令\n1.遥控选择命令","备用","备用","备用","备用","备用","0.不允许，有错误\n1.开关分\n2.开关合\n3.不允许，有错误"]
[null,"2字节","遥测","链路层传输顺序为低位在前，高位在后；低字节在前，高字节在后。如：69 01应该是01 69，即二进制0000 0001 0110 1001，转换成10进制是361"]
[null,"参数设置\n4字节","读取单个参数","在控制方向：空，在监视方向：返回参数（信息值为4个字节）"]
[null,null,"读取多个参数","在控制方向：空，在监视方向：返回参数（信息值1为4个字节，信息值n为4个字节）"]
[null,null,"预置/激活单个参数","在控制方向：参数值,在监视方向：返回参数镜像（信息值为4个字节）,后缀设定命令限定词1字节"]
[null,null,"预置/激活多个参数","在控制方向：参数值,在监视方向：返回参数镜像（信息值1为4个字节,信息值n为4个字节）,后缀设定命令限定词1字节"]
[null,"描述","总召唤无此项，时钟同步无此项，复位进程无此项，初始化结束无此项，"]
[]
["限定词","1字节","总召唤限定词",20]
[null,null,"复位进程限定词",1]
[null,null,"初始化原因","0.当地电源合上，1.当地手动复位，2.远方复位"]
[null,null,"品质描述词（遥测）","0（每个信息元素后缀1个字节）"]
[null,null,"设置命令限定词\n（参数预置）","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,null,"S/E","QL"]
[null,null,null,"1：选择预置参数\n0：执行激活参数","0:缺省值"]
[null,"描述","时钟同步无此项，遥信无此项，遥控无此项，"]
[]
["时标CP56Time2a\n","7字节","位","D7","D6","D5","D4","D3","D2","D1","D0"]
[null,null,"第1字节","毫秒(低8位)"]
[null,null,"第2字节","毫秒(高8位）"]
[null,null,"第3字节",0,0,"分钟(0~59）"]
[null,null,"第4字节",0,0,0,"小时（0~23）"]
[null,null,"第5字节","星期（1~7）",null,null,"日（0~31）"]
[null,null,"第6字节",0,0,0,0,"月（1~12）"]
[null,null,"第7字节",0,"年（0~99）"]
[null,"描述","时钟同步带时标、总召唤无时标、进程复位无时标、初始化结束无时标、参数设置无时标"]